Advanced Biogas Plant Setup for Smart Dairy Ltd.**

This project aims to establish a state-of-the-art biogas plant for Smart Dairy Ltd. in Bangladesh, utilizing cow dung from 300 cows to produce biogas, electricity, and biofertilizer. The system will meet the farm’s 40 kW electricity demand, cooking needs, and surplus biofertilizer for sale. Below is a detailed technical plan:

1. Feedstock Analysis & Biogas Potential :

- Daily cow dung : 300 cows × 15 kg/day =  4,500 kg/day .

- Biogas yield :

- Cow dung: 20–40 m³ biogas/ton (enhanced via co-digestion with food waste/grass, achieving  50 m³/ton ).

- Total biogas/day: 4.5 tons dung × 50 m³/ton =  225 m³/day .

-  Energy content : 225 m³ × 6 kWh/m³ =  1,350 kWh/day  (covers 40 kW × 24h =  960 kWh/day  with surplus).

2. Advanced Biogas Production Techniques :

A. Digester Design :

- Technology:  Continuous Stirred-Tank Reactor (CSTR)  with thermophilic digestion  (55°C) for faster conversion and higher yield.

- Retention time: 20 days.

-  Digester volume :

- Total slurry/day (4.5 tons dung + 4.5 tons water + 1 ton co-substrate) = 10 m³/day.

- Volume = 10 m³/day × 20 days = **200 m³**.

- Material: Reinforced concrete :

- Mixing system : Mechanical stirrers (e.g.,  submersible mixers ) for uniform slurry.

B. Gas Storage :

- Double-membrane roof: Integrates gas storage (no separate holder).

- Storage capacity : 225 m³/day ÷ 24h ≈ **9.4 m³/hour**. A 50 m³ membrane ensures a 5-hour buffer.

C. Co-Digestion :

- Add 1 ton/day:  of grass silage/food waste to boost methane by 20–30%.

3. Electricity Generation :

- Generator:  50 kW biogas CHP unit  (e.g., [Clarke Energy’s GE Jenbacher J312](https://www.clarke-energy.com/gas-type/biogas/)) with 40% electrical efficiency.

- Consumes 225 m³ × 0.25 m³/kWh = 56.25 m³/day for 40 kW load (surplus biogas for cooking).

Dewatering & Fertilizer System:

- Screw press separator (e.g., [BTS Biogas](https://www.bts-biogas.com/)):

- Processes 10 m³/day slurry into:

- Liquid fertilizer: 7 m³/day (direct field application).

- Solid biofertilizer : 3 m³/day (30% DM, sold as pellets).

4. Plant Setup Process :

Step 1: Site Preparation:

- Level land near cowshed; ensure proximity to slurry source and power grid.

Step 2: Digester Construction:

- Build 200 m³ CSTR digester with insulation for thermophilic conditions.

- Install mixing system and double-membrane roof.

Step 3: Gas Purification :

- Scrubber : Remove H₂S using iron oxide filters.

- Dehumidifier : Condense moisture from biogas.

Step 4: Generator Installation :

- Connect 50 kW CHP unit to farm grid; integrate gas pipelines.

Step 5: Digestate Management :

- Install screw press separator; link liquid fertilizer to irrigation.

5. Key Measurements :

- Digester: 200 m³ (e.g., cylindrical: 8m diameter × 4m height).

-  Inlet/outlet: 12-inch PVC pipes with slurry pumps.

- Gas pipes: 4-inch HDPE pipes for biogas transport.

6. Recommended Equipment & References :

- Generators: GE Jenbacher (Clarke Energy), [TEDOM](https://www.tedom.com/).

- Digester suppliers : [PlanET Biogas](https://www.planet-biogas.com/), [Hitachi Zosen Inova](https://www.hz-inova.com/).

- Guidelines: [IEA Bioenergy](https://www.ieabioenergy.com/), [FAO Biogas Handbook](http://www.fao.org/3/i3441e/i3441e.pdf).

7. Maintenance & Safety :

- Daily checks: Gas leaks, pH levels (maintain 6.8–7.5).

- Annual maintenance : Engine overhaul, membrane inspection.

- Safety : Flame arrestors, gas detectors (e.g., **MSA Ultima X5000**).

8. Expected Outputs :

- Biogas : 225 m³/day (1,350 kWh electricity + cooking fuel).

- Biofertilizer: 100 tons/year (30% sold commercially).

- CO2 reduction: ~300 tons/year.

This system ensures energy self-sufficiency, reduces waste, and generates revenue from surplus fertilizer. For detailed CAD designs, consulting firms like **BTS Biogas** or **PlanET Biogas**.

- Construct access roads for vehicles to reach key areas such as inlet/outlet points, storage facilities, and equipment for maintenance.

- Ensure utility lines (water, electricity) are routed appropriately to all necessary infrastructure, providing reliable services for operation.

4.  Gas Handling and Utilization:

4.1. Biogas Utilization:

- Designate specific biogas channels to kitchen facilities for direct cooking needs. Consider installing appropriate biogas stoves that are designed for higher efficiency and safety.

- Use biogas for heating water through specially designed boilers that can utilize low-calorific value gas effectively. This can be beneficial for washing equipment, sanitizing dairy tools, or heating animal bedding areas.

4.2. Gas Quality Control

- Install gas scrubbers to remove impurities such as hydrogen sulfide (H2S), carbon dioxide (CO2), and moisture from biogas before it is used in generators or cooking applications.

- Uses chemicals (like sodium hydroxide or iron salts) to react with and remove H2S, thereby improving overall gas quality.

- Employs bacteria to digest H2S and convert it to elemental sulfur or sulfate, suitable for more sustainable practices.

4.3. Safety Measures:

- Implement gas detection systems to monitor levels of methane and H2S in and around biogas equipment. Ensure alarms and emergency shutdown systems are in place to cut off gas supply in case of leaks or exceedance of safety limits.

- Regular maintenance checks should be scheduled to ensure integrity of gas pipelines, provided with pressure regulation to prevent overpressure conditions.

- Design biogas storage systems with appropriate safety valves, venting systems, and explosion-proof fixtures to mitigate risks associated with gas accumulation.

5. Electricity Generation:

5.1. Biogas Generator Selection:

- Opt for a biogas generator with 50 kW capacity, such as those manufactured by Jenbacher, Caterpillar, or MAN, known for their effectiveness in converting biogas to electricity.

- Features to consider include emission standards compliance, ease of maintenance, and fuel flexibility (ability to work with varying biogas quality and flow).

5.2. Installation Considerations:

- Employ a professionally designed layout that facilitates the installation of the generator and associated equipment (electrical switchgear, transformers) within a sheltered or controlled environment to protect against adverse weather.

- Ensure adequate ventilation surrounding the generator space to handle heat generated during operation and to avoid heat-related inefficiencies.

6. Fertilizer Processing:

6.1. Slurry Treatment and Nutrient Management:

The residual slurry (digestate) from the biogas digestion process contains valuable nutrients, including nitrogen, phosphorus, potassium, and other trace elements beneficial for soil health. The processing of this slurry into a marketable fertilizer product involves several key steps:

- Nutrient Analysis: Conduct a thorough nutrient analysis of the digestate to determine its nutrient composition. This helps in tailoring the fertilizer production process and developing suitable marketing materials showcasing the nutrient profile.

- Drying Options:

- Mechanical Drying: Implementing a mechanical drying system can efficiently reduce the moisture content of the digestate, making it suitable for storage and transport.

- Types of Dryers:

- Belt Dryer:  This type uses a continuous belt to convey the slurry over heated surfaces. The moisture evaporates, leaving behind drier material.  The **Belt Dryer by ANDRITZ  or Dupps Belt Dryer** can be sourced from companies specializing in industrial drying solutions.

- Rotary Drum Dryer:  A rotary dryer efficiently processes large quantities of slurry with continuous movement in a rotating drum. This technology utilizes hot air to achieve moisture evaporation.        Bühler rotary drum dryers  or  TurfCare’s rotary dryer  are examples that can be used for drying digestate effectively.

- Flash Dryer:  This equipment uses hot air to rapidly remove moisture from the digestate, ideal for high-quality dry fertilizer production. Consider Schutte-Buffalo’s Flash Dryer , which is suitable for quickly drying various organic materials.

- Post-Drying Processing: After drying, the product may be further processed to ensure uniform granule size or consistency. This can include milling or grinding processes to meet specific market requirements.